## database_no_np_with_chamber
[NodeName : FIX | Database : TK2 | File Name : C:\Users\Administrator\Desktop\TK2.csv | Date : 16.02.2023 | Time : 18:32:14]
#AI41 | DI97 | DO2#
[BLOCK TYPE | Tag | Next block | Description | Initial scan | Scan time | Smoothing | I/O device | H/W options | I/O address | Signal conditioning | Low EGU limit | High EGU limit | EGU tag | Initial A/M status | Alarm enable | Alarm area(s) | LOLO alarm limit | LO alarm limit | HI alarm limit | HIHI alarm limit | ROC alarm limit | Dead band | Alarm priority | Enable output | Security area 1 | Security area 2 | Security area 3 | Alarm area 1 | Alarm area 2 | Alarm area 3 | Alarm area 4 | Alarm area 5 | Alarm area 6 | Alarm area 7 | Alarm area 8 | Alarm area 9 | Alarm area 10 | Alarm area 11 | Alarm area 12 | Alarm area 13 | Alarm area 14 | Alarm area 15 | User field 1 | User field 2 | ESIG type | ESIG allow cont use | ESIG xmpt alarm ack | ESIG unsigned writes | ESIG cmnt required | PDR update rate | PDR access time | PDR deadband | PDR latch | PDR disable output | PDR array length | Hist tag description | Hist collect | Hist interval | Hist offset | Hist time resolution | Hist compression | Hist deadband | Hist compress type | Hist compress time | Scale enabled | Scale clamping | Scale use EGU | Scale raw low | Scale raw high | Scale low | Scale high | Shelve enable | Shelve policy]
!A_NAME | A_TAG | A_NEXT | A_DESC | A_ISCAN | A_SCANT | A_SMOTH | A_IODV | A_IOHT | A_IOAD | A_IOSC | A_ELO | A_EHI | A_EGUDESC | A_IAM | A_IENAB | A_ADI | A_LOLO | A_LO | A_HI | A_HIHI | A_ROC | A_DBAND | A_PRI | A_EOUT | A_SA1 | A_SA2 | A_SA3 | A_AREA1 | A_AREA2 | A_AREA3 | A_AREA4 | A_AREA5 | A_AREA6 | A_AREA7 | A_AREA8 | A_AREA9 | A_AREA10 | A_AREA11 | A_AREA12 | A_AREA13 | A_AREA14 | A_AREA15 | A_ALMEXT1 | A_ALMEXT2 | A_ESIGTYPE | A_ESIGCONT | A_ESIGACK | A_ESIGTRAP | A_ESIGREQ_COMMENT | A_PDR_UPDATERATE | A_PDR_ACCESSTIME | A_PDR_DEADBAND | A_PDR_LATCHDATA | A_PDR_DISABLEOUT | A_PDR_ARRAYLENGTH | A_HIST_DESC | A_HIST_COLLECT | A_HIST_INTERVAL | A_HIST_OFFSET | A_HIST_TIMERES | A_HIST_COMPRESS | A_HIST_DEADBAND | A_HIST_COMPTYPE | A_HIST_COMPTIME | A_SCALE_ENABLED | A_SCALE_CLAMP | A_SCALE_USEEGU | A_SCALE_RAWLOW | A_SCALE_RAWHIGH | A_SCALE_LOW | A_SCALE_HIGH | A_IALMSHLVENAB | A_ALMSHELVEPOLICY!
AI | DT1 |  | Показания датчика температуры ДТ1 | ON | 1 | 0 | SIM | Float | 1 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 25.0 | 30.0 | 0 | 1 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT1 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT2 |  | Показания датчика температуры ДТ2 | ON | 1 | 0 | SIM | Float | 2 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT2 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT3 |  | Показания датчика температуры ДТ3 | ON | 1 | 0 | SIM | Float | 3 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT3 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT4 |  | Показания датчика температуры ДТ4 | ON | 1 | 0 | SIM | Float | 4 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT4 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT5 |  | Показания датчика температуры ДТ5 | ON | 1 | 0 | SIM | Float | 5 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT5 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT6 |  | Показания датчика температуры ДТ6 | ON | 1 | 0 | SIM | Float | 6 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT6 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT7 |  | Показания датчика температуры ДТ7 | ON | 1 | 0 | SIM | Float | 7 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT7 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT8 |  | Показания датчика температуры ДТ8 | ON | 1 | 0 | SIM | Float | 8 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT8 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT9 |  | Показания датчика температуры ДТ9 | ON | 1 | 0 | SIM | Float | 9 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT9 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT10 |  | Показания датчика температуры ДТ10 | ON | 1 | 0 | SIM | Float | 10 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT10 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT11 |  | Показания датчика температуры ДТ11 | ON | 1 | 0 | SIM | Float | 11 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT11 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT12 |  | Показания датчика температуры ДТ12 | ON | 1 | 0 | SIM | Float | 12 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT12 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT13 |  | Показания датчика температуры ДТ13 | ON | 1 | 0 | SIM | Float | 13 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT13 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT14 |  | Показания датчика температуры ДТ14 | ON | 1 | 0 | SIM | Float | 14 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT14 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT15 |  | Показания датчика температуры ДТ15 | ON | 1 | 0 | SIM | Float | 15 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT15 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT16 |  | Показания датчика температуры ДТ16 | ON | 1 | 0 | SIM | Float | 16 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT16 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT17 |  | Показания датчика температуры ДТ17 | ON | 1 | 0 | SIM | Float | 17 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT17 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT18 |  | Показания датчика температуры ДТ18 | ON | 1 | 0 | SIM | Float | 18 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 25.0 | 30.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT18 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT19 |  | Показания датчика температуры ДТ19 | ON | 1 | 0 | SIM | Float | 19 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT19 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
20
AI | DT20 |  | Показания датчика температуры ДТ20 | ON | 1 | 0 | SIM | Float | 21 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT20 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT21 |  | Показания датчика температуры ДТ21 | ON | 1 | 0 | SIM | Float | 22 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT21 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT22 |  | Показания датчика температуры ДТ22 | ON | 1 | 0 | SIM | Float | 23 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT22 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT23 |  | Показания датчика температуры ДТ23 | ON | 1 | 0 | SIM | Float | 24 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT23 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | DT24 |  | Показания датчика температуры ДТ24 | ON | 1 | 0 | SIM | Float | 25 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 65.0 | 70.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DT | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DT24 | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | RegadaAI |  | Текущее положение клапана Regada 4-20мА | ON | 1 | 0 | SIM | Float | 27 | None | 0.0 | 24.0 |  | AUTO | ENABLE | NONE | 4.0 | 0 | 0 | 20.0 | 0 | 1 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Valve | Regada | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | RegadaAI | NO | 30 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0.0 | 24.0 | DISABLE
AI | DD1 |  | Показания датчика давления ДД1 | ON | 1 | 0 | SIM | Float | 28 | None | 0.0 | 600.0 |  | AUTO | ENABLE | NONE | 0 | 50.0 | 290.0 | 300.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DD | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DD1 | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | DD2 |  | Показания датчика давления ДД2 | ON | 1 | 0 | SIM | Float | 29 | None | 0.0 | 10.0 |  | AUTO | ENABLE | NONE | 0 | 1.0 | 4.0 | 5.0 | 0 | 0.5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DD | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DD2 | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 10 | DISABLE
AI | DD3 |  | Показания датчика давления ДД3 | ON | 1 | 0 | SIM | Float | 30 | None | 0.00 | 300 |  | AUTO | ENABLE | NONE | 1.0 | 5.0 | 50.0 | 300.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DD | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DD3 | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 600 | DISABLE
AI | DD4 |  | Показания датчика давления ДД4 | ON | 1 | 0 | SIM | Float | 31 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0.0 | 0.0 | 100.0 | 100.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | DD | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | DD4 | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | SU |  | Показания сигнализатора уровня СУ | ON | 1 | 0 | SIM | Float | 32 | None | 0.0 | 100 |  | AUTO | ENABLE | NONE | 0 | 0 | 100 | 100 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | LevelSensor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | SU | YES | 30 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | I_PTE |  | Показания тока индикации (мост с термопарой) ПИД регулятора 4-20мА | ON | 1 | 0 | SIM | Float | 33 | None | 0.0 | 100 |  | AUTO | ENABLE | NONE | 0 | 0 | 100 | 100 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | I_PTE | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | RegadaAQ |  | Уставка требуемой позиции клапана Regada 4-20мА | ON | 1 | 0 | SIM | Float | 34 | None | 0.0 | 24.0 |  | AUTO | ENABLE | NONE | 4.0 | 0 | 0 | 20.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | RegadaAQ | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0.0 | 24.0 | DISABLE
AI | PAC_TICS_COUNTER |  | пила от PLC | ON | 1 | 0 | SIM | SInt | 35 | None | 0 | 32 767 |  | AUTO | DISABLE | NONE | 0 | 0 | 32 767 | 32 767 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | Sensor | PLC | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | PAC_TICS_COUNTER | YES | 5 000.0 | 0 | Milliseconds | ENABLE | 0 | Percentage | 10 | NO | NO | YES | 0 | 65 535 | 0 | 32 767 | DISABLE
AI | PID_TEMP |  | actual temeprature in chamber | ON | 1 | 0 | SIM | Float | 37 | None | 0.0 | 1 600.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | PID_TEMP | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | RHM_1 |  | Cooling water consumption | ON | 1 | 0 | SIM | Float | 38 | None | 0.0 | 100.0 |  | AUTO | DISABLE | NONE | 0 | 50.00 | 58 | 60.00 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | Sensor | RHM | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | RHM_1 | YES | 5 000.0 | 0 | Milliseconds | ENABLE | 0 | Percentage | 10 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | TRZ |  | Natural gas consumption | ON | 1 | 0 | SIM | Float | 39 | None | 0.0 | 100.0 |  | AUTO | DISABLE | NONE | 3.0 | 5.0 | 35.0 | 40.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | Sensor | RHM | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | RHM_2 | YES | 5 000.0 | 0 | Milliseconds | ENABLE | 0 | Percentage | 10 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | ECS_WC_flowrate_IN |  | water flowrate at GF-2 furnace inlet | ON | 1 | 0 | SIM | Float | 40 | None | 0 | 100.0 |  | AUTO | DISABLE | NONE | 0 | 50.00 | 58 | 60.00 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_WC_flowrate_IN | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100.00 | DISABLE
AI | ECS_WC_temperature_IN |  | water temperature at GF-2 furnace reaction chamber inlet | ON | 1 | 0 | SIM | Float | 41 | None | 0.0 | 200.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 25.0 | 30.0 | 0 | 1 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_WC_temperature_IN | YES | 60 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100.0 | DISABLE
AI | ECS_WC_temperature_OUT |  | water temperature at GF-2 furnace reaction chamber outlet | ON | 1 | 0 | SIM | Float | 42 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 25.0 | 30.0 | 0 | 1 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_WC_temperature_OUT | YES | 60 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100.0 | DISABLE
AI | ECS_WC_flowrate_OUT |  | water flowrate at GF-2 furnace reaction chamber outlet | ON | 1 | 0 | SIM | Float | 43 | None | 0.0 | 100.0 |  | AUTO | DISABLE | NONE | 0 | 50.00 | 58 | 60.00 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_WC_flowrate_OUT | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100.00 | DISABLE
AI | ECS_GS_flowrate |  | natural gas flowrate at GF-2 furnace reaction chamber inlet | ON | 1 | 0 | SIM | Float | 44 | None | 0.0 | 100.0 |  | AUTO | DISABLE | NONE | 3.0 | 5.0 | 35.0 | 40.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | Gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_GS_flowrate | YES | 5 000.0 | 0 | Milliseconds | ENABLE | 0 | Percentage | 10 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | ECS_GS_pressure_in |  | natural gas pressure at GF-2 furnace reaction chamber inlet | ON | 1 | 0 | SIM | Float | 45 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0.0 | 0.0 | 100.0 | 100.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | ECS | Gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_GS_pressure_in | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | ECS_GS_temperature_in |  | natural gas temperature at GF-2 furnace reaction chamber inlet. | ON | 1 | 0 | SIM | Float | 46 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 25.0 | 30.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | Gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_GS_temperature_in | YES | 60 000.0 | 0 | Seconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 100 | DISABLE
AI | ECS_NS_flowrate |  | nitrogen flowrate at GF-2 furnace reaction chamber inlet | ON | 1 | 0 | SIM | Float | 47 | None | 0 | 100.0 |  | AUTO | DISABLE | NONE | 3.0 | 5.0 | 35.0 | 40.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | Nitrogen system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_NS_flowrate | YES | 1 000.0 | 0 | Milliseconds | ENABLE | 0 | Percentage | 10 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | ECS_NS_pressure_in |  | Vacuum pressure at GF-2 furnace reaction chamber inlet | ON | 1 | 0 | SIM | Float | 48 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 0.0 | 0.0 | 100.0 | 100.0 | 0 | 5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | ECS | Nitrogen system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_NS_pressure_in | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | ECS_VENT_CONSUMPTION |  | ventilation system CONSUMPTION | ON | 1 | 0 | SIM | Float | 50 | None | 0.0 | 1 200.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | ventilation system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_VENT_CONSUMPTION | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | ECS_PS_given_voltage_cotrol_signal |  | Indication of inlet of 4-20 мА | ON | 1 | 0 | SIM | Float | 51 | None | 0.0 | 40 |  | AUTO | ENABLE | NONE | 4 | 0 | 0 | 20 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_PS_given_voltage_cotrol_signal | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 40 | DISABLE
AI | ECS_PS_given_voltage |  | given voltage from CC | ON | 1 | 0 | SIM | Float | 52 | None | 0.0 | 40 |  | AUTO | ENABLE | NONE | 0.00 | 0 | 0 | 0 | 5.00 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_PS_given_voltage | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 40 | DISABLE
AI | ECS_PS_fact_current |  | Indication of current strength supplied to GF-2 furnace reaction chamber current leads | ON | 1 | 0 | SIM | Float | 53 | None | 0.0 | 60000 |  | AUTO | ENABLE | NONE | 0 | 0 | 0 | 0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_PS_fact_current | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 60000 | DISABLE
AI | ECS_PS_VOLTAGE |  | Indication of voltage supplied to GF-2 furnace reaction chamber current leads | ON | 1 | 0 | SIM | Float | 54 | None | 0.0 | 220 |  | AUTO | ENABLE | NONE | 0 | 0 | 0 | 0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_PS_VOLTAGE | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 220 | DISABLE
AI | ECS_VS_flowrate |  | vacuum system CONSUMPTION | ON | 1 | 0 | SIM | Float | 55 | None | 0.0 | 100.0 |  | AUTO | ENABLE | NONE | 5.0 | 0 | 0 | 40.0 | 0 | 0.5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | ECS | vacuum system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_VS_flowrate | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 100 | DISABLE
AI | ECS_VS_pressure |  | Vacuum pressure at GF-2 furnace reaction chamber inlet | ON | 1 | 0 | SIM | Float | 56 | None | 0.0 | 20.0 |  | AUTO | ENABLE | NONE | 0 | 1.0 | 5.0 | 10.0 | 0 | 0.5 | LOW | YES | NONE | NONE | NONE | ALL | [14 empty] | ECS | vacuum system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | ECS_VS_pressure | YES | 1 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535 | 0 | 10 | DISABLE
AI | PID_given_temp |  | temeprature givent by PID | ON | 1 | 0 | SIM | Float | 57 | None | 0.0 | 1 600.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | chamber_given_temp | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | PID_deviation_temp |  | chamber temeprature deviation from given | ON | 1 | 0 | SIM | Float | 58 | None | 0.0 | 1 600.0 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | chamber_given_temp | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | thermocouple_measured_position |  | measured position of thermocouple | ON | 1 | 0 | SIM | Float | 59 | None | 0.0 | 3200 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | TC | thermocouple | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | thermocouple_position | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | thermocouple_max_position_limit |  | MAX limit for position of thermocouple | ON | 1 | 0 | SIM | Float | 60 | None | 0.0 | 3200 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | TC | thermocouple | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | thermocouple_max_position_limit | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | thermocouple_min_position_limit |  | MIN limit position of thermocouple | ON | 1 | 0 | SIM | Float | 61 | None | 0.0 | 3200 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | TC | thermocouple | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | thermocouple_min_position_limit | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | thermocouple_given_position |  | given position of thermocouple | ON | 1 | 0 | SIM | Float | 62 | None | 0.0 | 3200 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | TC | thermocouple | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | thermocouple_given_position | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | thermocouple_remaining_time_for_replacement |  | timer for replacement of thermocouple | ON | 1 | 0 | SIM | Float | 63 | None | 0.0 | 3200 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | TC | thermocouple | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | thermocouple_remaining_time_for_replacement | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
AI | thermocouple_remaining_time_till_step |  | timer to move thermocouple on fixed step | ON | 1 | 0 | SIM | Float | 64 | None | 0.0 | 3200 |  | AUTO | ENABLE | NONE | 0 | 0 | 1 200.0 | 1 200.0 | 0 | 5 | LOW | NO | NONE | NONE | NONE | ALL | [14 empty] | TC | thermocouple | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | thermocouple_remaining_time_till_step | YES | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | NO | NO | YES | 0 | 65 535.0 | 0 | 1 200.0 | DISABLE
[BLOCK TYPE | Tag | Next block | Description | I/O device | H/W options | I/O address | Initial A/M status | Initial scan | Scan time | Invert output | Open tag | Close tag | Alarm enable | Alarm area(s) | Alarm priority | Alarm type | Event messages | Security area 1 | Security area 2 | Security area 3 | Enable output | Alarm area 1 | Alarm area 2 | Alarm area 3 | Alarm area 4 | Alarm area 5 | Alarm area 6 | Alarm area 7 | Alarm area 8 | Alarm area 9 | Alarm area 10 | Alarm area 11 | Alarm area 12 | Alarm area 13 | Alarm area 14 | Alarm area 15 | User field 1 | User field 2 | ESIG type | ESIG allow cont use | ESIG xmpt alarm ack | ESIG unsigned writes | ESIG cmnt required | PDR update rate | PDR access time | PDR deadband | PDR latch | PDR disable output | PDR array length | Hist tag description | Hist collect | Hist interval | Hist offset | Hist time resolution | Hist compression | Hist deadband | Hist compress type | Hist compress time | Shelve enable | Shelve policy]
!A_NAME | A_TAG | A_NEXT | A_DESC | A_IODV | A_IOHT | A_IOAD | A_IAM | A_ISCAN | A_SCANT | A_INV | A_OPENDESC | A_CLOSEDESC | A_IENAB | A_ADI | A_PRI | A_ALMCK | A_EVENT | A_SA1 | A_SA2 | A_SA3 | A_EOUT | A_AREA1 | A_AREA2 | A_AREA3 | A_AREA4 | A_AREA5 | A_AREA6 | A_AREA7 | A_AREA8 | A_AREA9 | A_AREA10 | A_AREA11 | A_AREA12 | A_AREA13 | A_AREA14 | A_AREA15 | A_ALMEXT1 | A_ALMEXT2 | A_ESIGTYPE | A_ESIGCONT | A_ESIGACK | A_ESIGTRAP | A_ESIGREQ_COMMENT | A_PDR_UPDATERATE | A_PDR_ACCESSTIME | A_PDR_DEADBAND | A_PDR_LATCHDATA | A_PDR_DISABLEOUT | A_PDR_ARRAYLENGTH | A_HIST_DESC | A_HIST_COLLECT | A_HIST_INTERVAL | A_HIST_OFFSET | A_HIST_TIMERES | A_HIST_COMPRESS | A_HIST_DEADBAND | A_HIST_COMPTYPE | A_HIST_COMPTIME | A_IALMSHLVENAB | A_ALMSHELVEPOLICY!
DI | ClosedK1 |  | Прием сигнала K1 закрыт | SIM |  | 65:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 | A20_DI00 | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenedK1 |  | Прием сигнала K1 открыт | SIM |  | 66:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | LocalK1 |  | Прием сигнала K1 в режиме местного управления | SIM |  | 67:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RemoteK1 |  | Прием сигнала K1 в режиме удаленного управления | SIM |  | 68:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | FaultK1 |  | Прием сигнала общего сбоя K1 | SIM |  | 69:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ReadyK1 |  | Прием сигнала общей готовности K1 | SIM |  | 70:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ReadyK2 |  | Прием сигнала сбоя К2. Программируемый. См. Руководство ULR1PAEX | SIM |  | 71:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | R1K2 |  | Прием сигнала открытого положения К2. Программируемый. См. Рук. | SIM |  | 72:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | R2K2 |  | Прием сигнала закрытого положения К2. Программируемый. См. Рук. | SIM |  | 73:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ClosedK3 |  | Прием сигнала K3 закрыт | SIM |  | 74:00 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenedK3 |  | Прием сигнала K3 открыт | SIM |  | 65:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | LocalK3 |  | Прием сигнала K3 в режиме местного управления | SIM |  | 66:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RemoteK3 |  | Прием сигнала K3 в режиме удаленного управления | SIM |  | 67:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | FaultK3 |  | Прием сигнала общего сбоя K3 | SIM |  | 68:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ReadyK3 |  | Прием сигнала общей готовности K3 | SIM |  | 69:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ClosedK4 |  | Прием сигнала K4 закрыт | SIM |  | 70:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenedK4 |  | Прием сигнала K4 открыт | SIM |  | 71:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | LocalK4 |  | Прием сигнала K4 в режиме местного управления | SIM |  | 72:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RemoteK4 |  | Прием сигнала K4 в режиме удаленного управления | SIM |  | 73:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | FaultK4 |  | Прием сигнала общего сбоя K4 | SIM |  | 74:01 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ReadyK4 |  | Прием сигнала общей готовности K4 | SIM |  | 65:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ClosedK5 |  | Прием сигнала K5 закрыт | SIM |  | 66:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenedK5 |  | Прием сигнала K5 открыт | SIM |  | 67:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | LocalK5 |  | Прием сигнала K5 в режиме местного управления | SIM |  | 68:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RemoteK5 |  | Прием сигнала K5 в режиме удаленного управления | SIM |  | 69:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | FaultK5 |  | Прием сигнала общего сбоя K5 | SIM |  | 70:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ReadyK5 |  | Прием сигнала общей готовности K5 | SIM |  | 71:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | A05_DI28 |  | Резерв KD. Уточнить назначение | SIM |  | 72:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | A05_DI29 |  | Резерв G1. Уточнить назначение | SIM |  | 73:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | A05_DI30 |  | Резерв G2. Уточнить назначение | SIM |  | 74:02 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | A05_DI31 |  | Резерв Fault KFD2. Уточнить назначение | SIM |  | 65:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RE5K2 |  | Свободно программируемое реле | SIM |  | 66:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RE4K2 |  | Свободно программируемое реле | SIM |  | 67:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RE3K2 |  | Свободно программируемое реле | SIM |  | 68:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RE2K2 |  | Свободно программируемое реле | SIM |  | 69:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | RE1K2 |  | Свободно программируемое реле | SIM |  | 70:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ReadyK2_RELAY |  | Свободно программируемое реле | SIM |  | 71:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve |  | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Y1PTE |  | Свободно программируемое реле событий Y1 ПИД регулятора. Уточнить | SIM |  | 72:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Y2PTE |  | Свободно программируемое реле событий Y2 ПИД регулятора. Уточнить | SIM |  | 73:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Y3PTE |  | Отклонение температуры более чем допустимое. ПИД регулятор | SIM |  | 74:03 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | PTE24 |  | ОШ ПИД регулятора. Уточнить назначение | SIM |  | 65:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Y6PTE |  | Авария ПИД регулятора | SIM |  | 66:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Cable1 |  | Контроль стыковки 1. Уточнить. | SIM |  | 67:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [15 empty] | Other | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Cable2 |  | Контроль стыковки 2. Уточнить. | SIM |  | 68:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [15 empty] | Other | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Cable3 |  | Контроль стыковки 3. Уточнить. | SIM |  | 69:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [15 empty] | Other | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Cable4 |  | Контроль стыковки 4. Уточнить. | SIM |  | 70:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [15 empty] | Other | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Cable5 |  | Контроль стыковки 5. Уточнить. | SIM |  | 71:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [15 empty] | Other | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | Cable6 |  | Контроль стыковки 6. Уточнить. | SIM |  | 72:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [15 empty] | Other | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_is_Connected |  | indicates connetion with ECS | SIM |  | 74:04 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ECS | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_Operation_permission |  | Permission for initiation of GF-2 CC operation | SIM |  | 65:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ECS | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_Malfunction |  | Indication for emergency completion of GF-2 CC operation | SIM |  | 66:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ECS | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_Emergency |  | Indication of noncritical failures in ECS | SIM |  | 67:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ECS | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_WC_on |  | water cooling IS running | SIM |  | 68:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_WC_off |  | water cooling IS stopped | SIM |  | 69:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_WC_ALARM |  | water cooling emergency | SIM |  | 70:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GS_ON |  | gas system IS running | SIM |  | 71:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GS_OFF |  | gas system IS stopped | SIM |  | 72:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GS_ALARM |  | gas system emergency | SIM |  | 73:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GS_GAS_CONCETRATION_norm |  | Concentration of natural gas does not exceed the normal value | SIM |  | 74:05 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GS_GAS_CONCETRATION_warning |  | Concentration of natural gas exceeds the normal value (warning indication) | SIM |  | 65:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GS_GAS_CONCETRATION_emergency |  | Concentration of natural gas exceeds the normal value (emergency indication) | SIM |  | 66:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_NS_ON |  | nitrogen system IS running | SIM |  | 67:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_NS_OFF |  | nitrogen system IS stopped | SIM |  | 68:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_NS_ALARM |  | nitrogen system emergency | SIM |  | 69:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VES_ON |  | valves energizing system IS running | SIM |  | 70:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | valves energizing | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VES_OFF |  | valves energizing system IS stopped | SIM |  | 71:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | valves energizing | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VES_ALARM |  | valves energizing system emergency | SIM |  | 72:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | valves energizing | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VENT_ON |  | ventilation system IS running | SIM |  | 73:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ventilation system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VENT_OFF |  | ventilation system IS stopped | SIM |  | 74:06 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ventilation system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VENT_ALARM |  | ventilation system emergency | SIM |  | 65:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ventilation system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_EGS_ON |  | exhaust gases system IS running | SIM |  | 66:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | exhaust gases system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_EGS_OFF |  | exhaust gases system IS stopped | SIM |  | 67:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | exhaust gases system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_EGS_ALARM |  | exhaust gases system emergency | SIM |  | 68:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | exhaust gases system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_PS_ON |  | power source IS running | SIM |  | 69:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_PS_OFF |  | power source IS stopped | SIM |  | 70:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_PS_ALARM |  | power source emergency | SIM |  | 71:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VS_ON |  | vacuum system IS running | SIM |  | 72:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | vacuum system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VS_OFF |  | vacuum system IS stopped | SIM |  | 73:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | vacuum system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VS_ALARM |  | vacuum system emergency | SIM |  | 74:07 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | vacuum system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | MOTOR_ON |  | thermocouple positioning motor is on | SIM |  | 65:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | TC | Motor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | MOTOR_OFF |  | thermocouple positioning motor is off | SIM |  | 66:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | TC | Motor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | MOTOR_blocked |  | thermocouple positioning motor is blocked | SIM |  | 67:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | TC | Motor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | MOTOR_ALARM |  | thermocouple positioning motor is in emergency condition | SIM |  | 68:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | TC | Motor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | PID_ON |  | PID is on | SIM |  | 69:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
70:08
DI | ISMAINDB |  |  | SIM |  | 71:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [16 empty] | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | CloseK1 |  | Выдача сигнала на закрытие К1 | SIM |  | 72:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenK1 |  | Выдача сигнала на открытие К1 | SIM |  | 73:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | StopK1 |  | Выдача сигнала на останов К1 | SIM |  | 74:08 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | CloseK2 |  | Выдача сигнала на закрытие К2 | SIM |  | 65:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenK2 |  | Выдача сигнала на открытие К2 | SIM |  | 66:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | StopK2 |  | Выдача сигнала на останов К2. Программируемый выход. См. Руководство | SIM |  | 67:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ESD2PK2 |  | Выдача сигнала 2P управление или 2P импульсное. См. Руководство | SIM |  | 68:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | CloseK3 |  | Выдача сигнала на закрытие К3 | SIM |  | 69:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenK3 |  | Выдача сигнала на открытие К3 | SIM |  | 70:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | StopK3 |  | Выдача сигнала на останов К3 | SIM |  | 71:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | CloseK4 |  | Выдача сигнала на закрытие К4 | SIM |  | 72:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenK4 |  | Выдача сигнала на открытие К4 | SIM |  | 73:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | StopK4 |  | Выдача сигнала на останов К4 | SIM |  | 74:09 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | CloseK5 |  | Выдача сигнала на закрытие К5 | SIM |  | 65:10 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | OpenK5 |  | Выдача сигнала на открытие К5 | SIM |  | 66:10 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | StopK5 |  | Выдача сигнала на останов К5 | SIM |  | 67:10 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Valve | Valve | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | D1_PTE |  | Управляющий сигнал D1 на ПИД регулятор. См. Руководство РТЭ-41Р | SIM |  | 68:10 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | D2_PTE |  | Управляющий сигнал D2 на ПИД регулятор. См. Руководство РТЭ-41Р | SIM |  | 69:10 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_WC_SET_ON |  | water cooling on command | SIM |  | 72:10 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | Water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_WC_SET_OFF |  | water cooling Off command | SIM |  | 73:10 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | Water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_WC_SET_Emerg_Stop |  | water cooling emergency Off command | SIM |  | 74:10 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | Water cooling | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GC_set_ON |  | gas system on command | SIM |  | 65:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GC_SET_OFF |  | gas system Off command | SIM |  | 66:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_GS_SET_Emerg_Stop |  | gas system emergency Off command | SIM |  | 67:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | gas system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VES_SET_ON |  | valves energizing system on command | SIM |  | 68:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | valves energizing | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VES_SET_OFF |  | valves energizing system Off command | SIM |  | 69:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | valves energizing | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VES_SET_Emerg_Stop |  | valves energizing system emergency Off command | SIM |  | 70:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | valves energizing | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VENT_SET_ON |  | ventilation system on command | SIM |  | 71:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ventilation | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VENT_SET_OFF |  | ventilation system Off command | SIM |  | 72:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ventilation | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VENT_SET_Emerg_Stop |  | ventilation system emergency Off command | SIM |  | 73:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | ventilation | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_EGS_SET_ON |  | exhaust gases system on command | SIM |  | 74:11 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | exhaust gases | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_EGS_SET_OFF |  | exhaust gases system Off command | SIM |  | 65:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | exhaust gases | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_EGS_SET_Emerg_Stop |  | exhaust gases system emergency Off command | SIM |  | 66:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | exhaust gases | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_PS_SET_ON |  | power source on command | SIM |  | 67:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_PS_SET_OFF |  | power source Off command | SIM |  | 68:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_PS_SET_Emerg_Stop |  | power source emergency Off command | SIM |  | 69:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | power source | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VS_SET_ON |  | vacuum system on command | SIM |  | 70:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | vacuum system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VS_SET_OFF |  | vacuum system Off command | SIM |  | 71:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | vacuum system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | ECS_VS_SET_Emerg_Stop |  | vacuum system emergency Off command | SIM |  | 72:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | ECS | vacuum system | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | PID_set_ON |  | enable PID processing | SIM |  | 73:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | PID_set_OFF |  | disable PID processing | SIM |  | 74:12 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | Sensor | PID | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | thermocouple_movement_set_on |  | enable thermocouple movement | SIM |  | 65:13 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | TC | Motor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | thermocouple_movement_set_off |  | enable thermocouple movement | SIM |  | 66:13 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | TC | Motor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | thermocouple_run_to |  | move thermocouple to given position | SIM |  | 67:13 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | TC | Motor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
DI | thermocouple_set_current_position |  | set thermocouple position measured outside the system | SIM |  | 68:13 | AUTO | ON | 1 | NO | Off | On | ENABLE | NONE | LOW | COS | DISABLE | NONE | NONE | NONE | YES | ALL | [14 empty] | TC | Motor | NONE | YES | NO | REJECT | NO | 1 000 | 300 000 | 0 | NO | NO | 0 |  | NO | 5 000.0 | 0 | Milliseconds | DISABLE | 0 | Absolute | 0 | DISABLE
[-------------------------------------------------End of Block List-------------------------------------------------]

## Лист1
GF-2 | − | реакционная камера печи типа ГФ-2 (находится в сфере ответственности ГП «КБ «Южное»)
AS | − | система подачи азота (находится в сфере ответственности Заказчика).
СС | − | пульт управления (входит в состав реакционной камеры печи типа ГФ-2, находится в сфере ответственности ГП «КБ «Южное»)
CS | − | система водяного охлаждения (находится в сфере ответственности Заказчика)
CVS | − | система цеховой вентиляции (находится в сфере ответственности Заказчика)
DP | − | габариты реакционной камеры печи типа ГФ-2 (находится в сфере ответственности ГП «КБ «Южное»)
ECS | − | система управления общецеховым оборудованием (находится в сфере ответственности Заказчика)
EGRS | − | система цеховой утилизации отработанных газов (находится в сфере ответственности Заказчика)
GSS | − | система подачи природного газа (находится в сфере ответственности Заказчика)
G | − | заземление (находится в сфере ответственности Заказчика)
IoCF | − | монтажные размеры для крепления реакционной камеры печи типа ГФ-2 к бетонному полу на участке пиролитического уплотнения (находится в сфере ответственности ГП «КБ «Южное»)
PCC | − | питание пульта управления реакционной камеры печи типа ГФ-2 (находится в сфере ответственности Заказчика)
PEV | − | питание электроприводов клапанов реакционной камеры печи типа ГФ-2 (находится в сфере ответственности Заказчика)
PS | − | источник электропитания реакционной камеры печи типа ГФ-2 с силовыми шинами для подключения токоподводов (находится в сфере ответственности Заказчика)
VS | − | общецеховая система вакуумирования (находится в сфере ответственности Заказчика)